A Comparative Study of IEC 76 and ANSI C57.12 on Transformers

# John K. John, Member, IEEE

# Subhas Sarkar, Senior Member, IEEE

Abstract-  This paper presents a brief comparison of major parameters like service conditions, categories, impedance, temperature rises, tolerance, dielectric insulation levels, test requirements etc of transformers in IEC 76 and IEEE/ANSI C57.The understanding of IEC 76 is important for the transformer market outside USA as most of  the new market are looking for transformers conforming to IEC specification. An attempt is made in this paper to have a quick understanding of important technical parameters of transformers per IEC 76, in comparison with IEEE/ANSI C57.  Clause numbers in both specifications are mentioned against the parameters for easy reference for the readers.  Because of the volume of the standards and details included in individual sections, it is difficult to cover a detailed comparison in a technical paper.  Only major parameters which are commonly encountered in inquiry, order, manufacturing, and of testing of power transformers are covered in this paper.

# Introduction

A vision of next century brings into focus the expanding horizons leading to globalization. Two of the major standards for transformers are the ANSI/IEEE and the IEC. Efforts are going on at various levels to harmonize them. This paper  intends to add to the efforts by bringing out a comparison of  IEC and ANSI standards , which is presented in a tabular form.  The main emphasis is given for liquid filled transformers. However, wherever separate clauses are available, details have been provided for dry-type . The ANSI/IEEE standards and the IEC standards on transformers are very elaborate and hence, it is not the intention in this paper to elaborate all the technical parameters. Most important parameters are brought out and the clause numbers in both standards are given for reader’s reference. Wherever possible brief description of the parameters as well as remarks for comparison also are added.  The system voltages, BILs  etc are different in the two standards and this results in a number of related changes in the determination of  test levels and component selection. This paper will be of interest to those who are looking for a quick comparison of the standards, without going into much details. Also it is intended as a reference for the different clauses in both ANSI/IEEE and IEC.

| Standards Features | IEC | ANSI/IEEE | REMARKS |
| --- | --- | --- | --- |
| 1. Usual Service Conditions 1.1 Altitude 1.2 Temperature of Ambient Air and Cooling Medium 1.2.1 For water cooled 1.2.2 For air cooled air temp. 1.3 Supply Voltage 1.4 Load Current 1.5 Step-Down Operation | IEC 76-1 Clause 1.2.1 A height above sea level not exceeding 1000m (3300 ft) Not exceeding 25o C at inlet Not above 40o C not below -25o C Further limitations per IEC 76-2 for oil-immersed transformers and IEC 726 for dry type transformers. Approx. sinusoidal and symmetrical 5% Total harmonic content,1%even harmonic content. - | C57.12.01- Dry Type Trfs. (Including those with cast and resin encapsulated) Clause 4.1 C57.12.00- Liquid Immersed Trfs. Clause 4.1 The altitude shall not exceed 3300 ft (1000 m) Shall not exceed 30o C and the average temp. of cooling water shall not exceed 25o C for any 24 hour period. Minimum water temp. shall not be lower than 1o C unless the cooling water includes anti-freeze suitable for -20o C operation. Not exceeding 40o C and the average temperature of cooling air for any 24 h period shall not exceed 30oC. Top liquid temperature of transformer (when operating) shall not be lower than 20oC. The min. ambient temp.shall not be lower than-30 oC for dry type units Approx. sinusoidal and symmetrical 5% Harmonic factor Trfs shall be for step down operation , unless otherwise specified | Service conditions specified in both stds are comparable |
| Standards Features | IEC | ANSI/IEEE | REMARKS |
| 2 Unusual Service Conditions 2.1 Unusual Loading 2.2 Unusual Altitude 2.3 Operation above rated voltage 3. Categories of transformers 3.1 KVA Basis CAT 1 CAT 2 CAT 3 CAT 4 3.2 Voltage Basis 4. Ratings KVA | IEC 76-1 Clause 1.2.2 IEC 76-2 Clause 4.4 If exceeds 1000M (3300ft) Limit of temp-rise per clause 4.3 of IEC 76-2 External insulation at high altitude per IEC 76-3 and 76-3-1 for oil trf. and IEC 726 for dry type. Should deliver rated current at an applied voltage equal to 105% of rated voltage Clause 1.2.1.1 of IEC 76-5 Up to 3150 KVA 3151-40000 KVA Above40000 KVA - There is no categorized basis in IEC. Clause 4.1 of IEC 76-1 Highest KVA is the rated KVA of a trfr | C57.12.01- Clause 4.2 C57.12.00- Clause 4.3 C57.96 for dry type C57.91 and 92 for oil type Altitude correction factor for dielectric strength table 1 of C57.12.01 C57.12.00 Deliver rated output at 5% above rated secondary voltage or volts/Hz without exceeding temp. rise. Operate 10% above rated secondary voltage or volts/Hz at no load without exceeding temp. rise. Clause 12.1 C57.12.90 ; 12.91 1 phase 3 phase 1-500 KVA 15-500KVA 501-1667 501-5000 1668-10000 5001-30000 Above 10000 Above 30000 (Liquid type) Clause 5.10 C57.12.00 Liquid type Class 1 power transformer 69 KV and below Class 2 power transformer 115 KV thru 765 KV Clause 5.4 of C57.12.00, C57.12.01 Several rated KVA | Both stds same |

| Standards Features | IEC | ANSI/IEEE | REMARKS |
| --- | --- | --- | --- |
| KVA Over-excitation 5. Impedance | Impedance and load losses at top rating IEC 76-1 Clause 4.1 Input power at rated primary voltage IEC 76-1 Clause 4.4 5% at full load Table1 of IEC 76-5 Rated KVA % Up to 630 4.0 631-1250 5.0 1251-3150 6.25 3151-6300 7.15 6301-12500 8.35 12501-25000 10.0 25001-200000 12.5 . | Impedance and load losses at base rating C57.12.00- Clause 5.4 C57-12.01 Output power at rated secondary voltage C57.12.00, C57.12.01 Clause 4.1.6 5% at full load 10% at no load A) Dry type Table 4.C57.12.51 1981 HV BIL LV VOLTAGE KV < 600 V >2400 < 60 5.75 5.75 > 60 By discussion between user and manufacturer B) Oil Filled Table 10, C57.12.10 Without LTC With LTC HV LV LV 2400 LV 2400and BIL 420V and above above 60-110 5.75 5.5 --- 150 6.75 6.5 7.0 200 7.25 7.0 7.5 250 7.75 7.5 8.0 350 ----- 8.0 8.5 450 ----- 8.5 9.0 550 ----- 9.0 9.5 650 ----- 9.5 10.0 750 ----- 10.0 10.5 * For transformers > 5000 KVA self cooled, these shall be same as those for 150 BIL. | In IEC typical impedance values are specified based on KVA rating ANSI has categorized the figures based on HV BIL, LV Voltage and whether it is with or without LTC |

| Standards Features | IEC | ANSI/IEEE | REMARKS |
| --- | --- | --- | --- |
| 6. Temperature Rise 6.1 Identification Symbol 6.1.1 Dry Type Ventilated self-cooled Ventilated forced-air- cooled Ventilated self -cooled/ forced-air-cooled Nonventilated self - cooled Sealed self-cooled Sealed forced-cooled 6.1.2 Liquid Immersed Self Cooled Self-cooled/ forced air- cooled Self-cooled/ forced air- cooled/ forced liquid- cooled | IEC 726, Clause 9.1 AN AF ANAF ANAN GNAN GNAF IEC 76-2 Clause 3 Four-letter code as described in this clause. Examples: ONAN ONAN/ONAF ONAN/ONAF/OFAF | C57. 12.01 Clause 5.1 AA AFA AA/FA ANV GA C57.12.00 Clause 5.1 OA OA/FA OA/FA/FOA | IEC has no specific symbol for sealed self cooled type. IEC has symbols for other cooling media also; refer to 76-2, Clause 3. |

| Standards Features | IEC | ANSI/IEEE | REMARKS |
| --- | --- | --- | --- |
| Temperature- Rise Limits 6.2.1 Dry Type Wdg. Temp. Rise by Resistance in oC. Core and Parts Liquid Type Average Wdg. Temp. Rise in oC. Top Oil Rise oC. Core and Parts | Table IV IEC 726 Temp. class Max. of insulation temp. rise of wdg. A(105) 60 E(120) 75 B(130) 80 F(155) 100 H(185) 125 C(220) 150 Shall not reach a value that will damage core and other parts. IEC 76-2 clause 4.2 Natural or forced non-directed oil circulation: 65 Forced and directed oil circulation: 70 60 Shall not reach a value that will damage adjacent parts or undue aging of oil. | Table 4a, C57.12.01 Temp. of Average wdg. Insu. System temp. rise 130 60 150 80 185 115 200 130 220 150 Less than values that would impair the functional capability. Clause 5.11, C57.12.00 65 (80 max. Hottest-spot temp. rise.) 65 Shall not attain excessive temp. rises at maximum rated load. | ANSI Specifies oil temp. rise same as that of winding. |

| Standards Features | IEC | ANSI/IEEE | REMARKS |
| --- | --- | --- | --- |
| Tolerances 7.1 Voltage ratio Impedance 2 Wdg. 3 Wdg. Or more. Auto Trf. Losses No load Load Total losses No load current | Table 1 of IEC 76-1 Lower of a) +0.5% of declared ratio. b) + 1/10 of the actual percentage impedance on the principal tapping. Both oil and dry type. + 7.5% when the impedance is > 10% + 10% when the impedance is < 10% + 10% for one specified pair + 15% for second specified pair. + 10% on principal tapping. + 15% on any other tapping. All units + 15%, provided tolerance for total loss is not exceeded. Same as no load +10% *Applicable for component losses. +30% | Clause 9.0, C57.12.00 C57.12.01 + 0.5% Dry type Oil filled + 7.5% 7.5% if IZ% >2.5 10% if IZ% <2.5 + 10% + 10% + 10% + 10% No. of units in one order 1 2 or more each avg. unit + 10 +10 0 +6% +6% 0 ANSI is silent on this. | Both STD’s the same. IEC is more slack than ANSI. IEC is more slack than ANSI. |

| Standards Features | IEC | ANSI/IEEE | REMARKS |
| --- | --- | --- | --- |
| Dielectric insulation level. Lightning impulse and Power Frequency Test Level. Switching surge test levels. 8.3 External clearances in air. Tests Routine Tests Design/Type tests 9.3 Special tests | IEC 76-3 Tables 2,3,4 and 5 76-3 Table 5 76-3-1 76-1, clause 10.1.1 76-1, clause 10.1.2 76-1, clause 10.1.3 | C57.12.00 Table 3,4 and 5 C57.12.00 Table 5 C57.12.00 Table 2 C57.12.00 Table 16 C57.12.01 Table 7 C57.12.00 Table 16 C57.12.01 Table 7 C57.12.00 Table 16 C57.12.01 Table 7 | . Both standards are similar. Generally IEC levels are lower for several voltage classes. ANSI starts at 115 KV and typically higher than IEC. IEC starts at 300 KV. Both standards are similar. Resistance, impedance and load loss measurement are not routine tests for 500KVA or smaller per ANSI. Lightning Impulse test is routine for class 2 power transformer per ANSI. Resistance, Impedance and load loss measurement are design tests for 500 KVA or smaller, per ANSI. Sound level is a special test per IEC. |

| Standards Features | IEC | ANSI/IEEE | REMARKS |
| --- | --- | --- | --- |
| Connection and phase displacement symbols Rating plates information. 12. Accessories | Clause 6, IEC 76-1 Annex. D, IEC 76-1 Clause 7, IEC 76-1 IEC 76 doesn’t contain a list of standard accessories. | Fig1, C57.12.00 C57.12.01 Table 9,C57.12.00 Table 5, C57.12.01 Table 11, C57.12.10 |  |

# Conclusion

The study concludes that there is not much difference in the specification for the active parts of the transformer i.e. core and coil. Minor differences are there in the case of testing and tolerances. Major differences are in the accessories, which are not covered in detail in this paper. Many mechanical details are well covered in ANSI, whereas there may not be adequate references to many such details in IEC. ANSI/IEEE includes more tutorial / educational texts and hence is more user oriented.  IEC’S latest versions include more details but still it leaves many details to mutual agreements between manufacturer and user.

The authors acknowledge that in order to limit the size of the paper they could not include all the details for a comprehensive comparison of the two standards.

Authors plan to work on a more detailed comparative study in future. The proposed study will include special areas like testing procedure comparisons, special duty transformers etc. in addition to elaboration of different parameters already covered in this paper.

# Acknowledgment

The authors thank the management of Virginia Transformer Corp. for giving the permission to publish this work, which was originally prepared as an in-house training document.

# Biographies (updated ‘01)

John .K. John obtained his B.S degree in Electrical Engineering  with Honors  from Kerala University, India in  1974. He has more than 23 years experience in transformer design and manufacturing. He is working with Virginia Transformer Corp. in Roanoke, Virginia since 1993 and is presently holding the position of  Technical Manager. He is member IEEE and a Chartered Engineer in India.

Subhas Sarkar obtained his BSEE  degree from Regional Engg college, Durgapur, India in 1966 and M.TECH degree from Indian Institute of Technology, Kharagpur in 1968. He has nearly thirty years of experience, mostly in the area of transformer design and manufacturing. He had a brief  stint  in teaching.  He has authored two books on electronic  devices and circuits, and has published nearly twenty papers.

He is working with Virginia Transformer Corp. since 1992 and is presently holding the position of Director of Engineering. He is senior member of IEEE  since 1993. He is a registered Professional Engineer in the state of  Virginia.